## SWMS
1. Choose the type of SWMS | [5 empty] | Simplified Storm Water Management System Notes
2 |  |  | STORM WATER MANAGEMENT SYSTEM (SWMS) PIPE LAYOUT & SYSTEM DATA |  |  | A simplified system is rectangular with two manifolds (see sketch below).
2. Type in below the total amount of storage volume required (ft³) |  |  |  | SWMS Type | Retention | Retention implies groundwater infiltration using fully perforated pipe.
| Corrugated Metal Pipe (CMP) |  | Storage Volume Required (ft³) |  | 35400
|  |  | Pipe Diameter (inches) |  | 60 | Entire SWMS of the same size pipe (manifolds/laterals of same diameter).
35400 |  |  | No. of Laterals |  | 10
| Diameter of Pipe (ft) |  |  |  | 5
3. Choose pipe diameter (in) | Cross-Sectional Area of Pipe (ft2) |  |  |  | 19.635 | Cross-sectional area (ft2) is the same as the volume per foot of pipe (ft3/ft).
7 | Minimum Lateral Spacing (ft) |  |  |  | 2.5 | Minimum spacing between sides of pipe per AASHTO 12.6.7.
| Stone Storage Above Pipe (ft) |  |  |  | 1 | As available for infiltration systems.
| 6-in bedding | backfill 12-in above pipe |  | Bedding (ft) | 0.5 | Bedding used as part of the storage depth for retention systems.
4. Choose the number of laterals |  |  | Storage Depth (ft) |  | 6.5 | Bedding thickness + Pipe OD + storage above pipe.
10 |  |  | Backfill Void Ratio |  | 40% | 40% porosity for washed, open graded, angular aggregate.
| 6.5 |  | Manifold Length (ft) |  | 72.5
|  |  | Lateral Length (ft) |  | 97.5883 | Length of each lateral between manifolds.
5. Choose bedding depth (ft) |  |  | Total Pipe Length (ft) |  | 1120.8829 | Theoretical length of pipe needed for the entire SWMS (manifolds and laterals).
0.5 | 2 | 2.5 | Excavation Width (ft) |  | 76.5 | Includes an additional 2-ft from the edge of pipe along each side of the SWMS.
|  | above dimensions in feet | Excavation Length (ft) |  | 111.5883 | Includes an additional 2-ft from the edge of pipe on each end of the SWMS.
6. Choose amount of stone storage above pipe (ft) |  |  | Stone Required (yd3) |  | 1239.9552 | Total amount of stone if backfilling to a height of 1-ft above top of pipe (recommended).
| Pipe Storage Volume Provided (ft3) |  |  |  | 22008.4834
1 | Stone Storage Volume Provided (ft3) |  |  |  | 13391.5166 | See storage depth note above.
| Total Volume Provided (ft3) |  |  |  | 35400
| 60 | -in Diameter CMP |  |  | 10 | Laterals | Excavation Footprint | 8536.5038 | sf
| Fully Perforated Retention System | [5 empty] | System Footprint | 7800.1507 | sf
System Length (ft)
107.5883
76.5
| Excavation | [7 empty] | 72.5
| Width (ft) | [7 empty] | System
Width (ft)
111.5883
Excavation Length (ft)

## Data
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
F6 | CMP PARAMETERS
| Pipe Diameter |  | Minimum | Area | Minimum | Minimum Spacing (ft) |  | 1 | Detention
| (in) | (ft) | Spacing (ft) | (sf) | Cover (ft) | ASTM | AASHTO | 2 | Retention
1 | 24 | 2 | 1 | 3.1416 | 1 | 2 | 1
2 | 30 | 2.5 | 1.25 | 4.9087 | 1 | 2 | 1.25
3 | 36 | 3 | 1.5 | 7.0686 | 1 | 2 | 1.5
4 | 42 | 3.5 | 1.75 | 9.6211 | 1 | 2 | 1.75
5 | 48 | 4 | 2 | 12.5664 | 1 | 2 | 2 |  | 0.33
6 | 54 | 4.5 | 2.25 | 15.9043 | 1 | 2.25 | 2.25 |  | 0.5
7 | 60 | 5 | 2.5 | 19.635 | 1 | 2.5 | 2.5 |  | 0.75
8 | 66 | 5.5 | 2.75 | 23.7583 | 1 | 2.75 | 2.75 |  | 1
9 | 72 | 6 | 3 | 28.2743 | 1 | 3 | 3
10 | 78 | 6.5 | 3 | 33.1831 | 1 | 3 | 3
11 | 84 | 7 | 3 | 38.4845 | 1 | 3 | 3
12 | 90 | 7.5 | 3 | 44.1786 | 1 | 3 | 3
13 | 96 | 8 | 3 | 50.2655 | 1 | 3 | 3
14 | 102 | 8.5 | 3 | 56.745 | 1.0625 | 3 | 3
15 | 108 | 9 | 3 | 63.6173 | 1.125 | 3 | 3
16 | 114 | 9.5 | 3 | 70.8822 | 1.1875 | 3 | 3
17 | 120 | 10 | 3 | 78.5398 | 1.25 | 3 | 3
18 | 126 | 10.5 | 3 | 86.5901 | 1.3125 | 3 | 3
19 | 132 | 11 | 3 | 95.0332 | 1.375 | 3 | 3
20 | 138 | 11.5 | 3 | 103.8689 | 1.4375 | 3 | 3
21 | 144 | 12 | 3 | 113.0973 | 1.5 | 3 | 3